## Sheet1
No. | LEN | ENERGY METER DATA | [5 empty] | TIA PORTAL DATA | [5 empty] | Len
|  | Description | Register | Units | Size (INT16) | Data Type | Access | Description | Register | Units | Size (INT16) | Data Type | Access | 112
1 | 0 | Current A | 3000 | A | 2 | FLOAT32 | R | Current A | 43000 | A | 2 | FLOAT32 | R
2 | 4 | Current B | 3002 | A | 2 | FLOAT32 | R | Current B | 43002 | A | 2 | FLOAT32 | R
3 | 8 | Current C | 3004 | A | 2 | FLOAT32 | R | Current C | 43004 | A | 2 | FLOAT32 | R
4 | 12 | Current N | 3006 | A | 2 | FLOAT32 | R | Current N | 43006 | A | 2 | FLOAT32 | R
5 | 16 | Current G | 3008 | A | 2 | FLOAT32 | R | Current G | 43008 | A | 2 | FLOAT32 | R
6 | 20 | Current Avg | 3010 | A | 2 | FLOAT32 | R | Current Avg | 43010 | A | 2 | FLOAT32 | R
7 | 24 | Current Unbalance A | 3012 | % | 2 | FLOAT32 | R | Current Unbalance A | 43012 | % | 2 | FLOAT32 | R
8 | 28 | Current Unbalance B | 3014 | % | 2 | FLOAT32 | R | Current Unbalance B | 43014 | % | 2 | FLOAT32 | R
9 | 32 | Current Unbalance C | 3016 | % | 2 | FLOAT32 | R | Current Unbalance C | 43016 | % | 2 | FLOAT32 | R
10 | 36 | Current Unbalance Worst | 3018 | % | 2 | FLOAT32 | R | Current Unbalance Worst | 43018 | % | 2 | FLOAT32 | R
11 | 40 | Voltage A-B | 3020 | V | 2 | FLOAT32 | R | Voltage A-B | 43020 | V | 2 | FLOAT32 | R
12 | 44 | Voltage B-C | 3022 | V | 2 | FLOAT32 | R | Voltage B-C | 43022 | V | 2 | FLOAT32 | R
13 | 48 | Voltage C-A | 3024 | V | 2 | FLOAT32 | R | Voltage C-A | 43024 | V | 2 | FLOAT32 | R
14 | 52 | Voltage L-L Avg | 3026 | V | 2 | FLOAT32 | R | Voltage L-L Avg | 43026 | V | 2 | FLOAT32 | R
15 | 56 | Voltage A-N | 3028 | V | 2 | FLOAT32 | R | Voltage A-N | 43028 | V | 2 | FLOAT32 | R
16 | 60 | Voltage B-N | 3030 | V | 2 | FLOAT32 | R | Voltage B-N | 43030 | V | 2 | FLOAT32 | R
17 | 64 | Voltage C-N | 3032 | V | 2 | FLOAT32 | R | Voltage C-N | 43032 | V | 2 | FLOAT32 | R
18 | 68 | Not use | 3034 | --- | - | - | - | - | 43034 | --- | - | - | -
19 | 72 | Voltage L-N Avg | 3036 | V | 2 | FLOAT32 | R | Voltage L-N Avg | 43036 | V | 2 | FLOAT32 | R
20 | 76 | Voltage Unbalance A-B | 3038 | % | 2 | FLOAT32 | R | Voltage Unbalance A-B | 43038 | % | 2 | FLOAT32 | R
21 | 80 | Voltage Unbalance B-C | 3040 | % | 2 | FLOAT32 | R | Voltage Unbalance B-C | 43040 | % | 2 | FLOAT32 | R
22 | 84 | Voltage Unbalance C-A | 3042 | % | 2 | FLOAT32 | R | Voltage Unbalance C-A | 43042 | % | 2 | FLOAT32 | R
23 | 88 | Voltage Unbalance L-L Worst | 3044 | % | 2 | FLOAT32 | R | Voltage Unbalance L-L Worst | 43044 | % | 2 | FLOAT32 | R
24 | 92 | Voltage Unbalance A-N | 3046 | % | 2 | FLOAT32 | R | Voltage Unbalance A-N | 43046 | % | 2 | FLOAT32 | R
25 | 96 | Voltage Unbalance B-N | 3048 | % | 2 | FLOAT32 | R | Voltage Unbalance B-N | 43048 | % | 2 | FLOAT32 | R
26 | 100 | Voltage Unbalance C-N | 3050 | % | 2 | FLOAT32 | R | Voltage Unbalance C-N | 43050 | % | 2 | FLOAT32 | R
27 | 104 | Voltage Unbalance L-N Worst | 3052 | % | 2 | FLOAT32 | R | Voltage Unbalance L-N Worst | 43052 | % | 2 | FLOAT32 | R
28 | 108 | Active Power A | 3054 | kW | 2 | FLOAT32 | R | Active Power A | 43054 | kW | 2 | FLOAT32 | R
29 | 112 | Active Power B | 3056 | kW | 2 | FLOAT32 | R | Active Power B | 43056 | kW | 2 | FLOAT32 | R
30 | 116 | Active Power C | 3058 | kW | 2 | FLOAT32 | R | Active Power C | 43058 | kW | 2 | FLOAT32 | R
31 | 120 | Active Power Total | 3060 | kW | 2 | FLOAT32 | R | Active Power Total | 43060 | kW | 2 | FLOAT32 | R
32 | 124 | Reactive Power A | 3062 | kVAR | 2 | FLOAT32 | R | Reactive Power A | 43062 | kVAR | 2 | FLOAT32 | R
33 | 128 | Reactive Power B | 3064 | kVAR | 2 | FLOAT32 | R | Reactive Power B | 43064 | kVAR | 2 | FLOAT32 | R
34 | 132 | Reactive Power C | 3066 | kVAR | 2 | FLOAT32 | R | Reactive Power C | 43066 | kVAR | 2 | FLOAT32 | R
35 | 136 | Reactive Power Total | 3068 | kVAR | 2 | FLOAT32 | R | Reactive Power Total | 43068 | kVAR | 2 | FLOAT32 | R
36 | 140 | Apparent Power A | 3070 | kVA | 2 | FLOAT32 | R | Apparent Power A | 43070 | kVA | 2 | FLOAT32 | R
37 | 144 | Apparent Power B | 3072 | kVA | 2 | FLOAT32 | R | Apparent Power B | 43072 | kVA | 2 | FLOAT32 | R
38 | 148 | Apparent Power C | 3074 | kVA | 2 | FLOAT32 | R | Apparent Power C | 43074 | kVA | 2 | FLOAT32 | R
39 | 152 | Apparent Power Total | 3076 | kVA | 2 | FLOAT32 | R | Apparent Power Total | 43076 | kVA | 2 | FLOAT32 | R
40 | 156 | Not use | Not use
41 | 160 | Not use | Not use
42 | 164 | Not use | Not use
43 | 168 | Not use | Not use
44 | 172 | Not use | Not use
45 | 176 | Not use | Not use
46 | 180 | Not use | Not use
47 | 184 | Not use | Not use
48 | 188 | Power Factor A | 3078 | --- | 2 | 4Q_FP_PF | R | Power Factor A | 43078 | --- | 2 | 4Q_FP_PF | R
49 | 192 | Power Factor B | 3080 | --- | 2 | 4Q_FP_PF | R | Power Factor B | 43080 | --- | 2 | 4Q_FP_PF | R
50 | 196 | Power Factor C | 3082 | --- | 2 | 4Q_FP_PF | R | Power Factor C | 43082 | --- | 2 | 4Q_FP_PF | R
51 | 200 | Power Factor Total | 3084 | --- | 2 | 4Q_FP_PF | R | Power Factor Total | 43084 | --- | 2 | 4Q_FP_PF | R
52 | 204 | Displacement Power Factor A | 3086 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor A | 43086 | --- | 2 | 4Q_FP_PF | R
53 | 208 | Displacement Power Factor B | 3088 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor B | 43088 | --- | 2 | 4Q_FP_PF | R
54 | 212 | Displacement Power Factor C | 3090 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor C | 43090 | --- | 2 | 4Q_FP_PF | R
55 | 216 | Displacement Power Factor Total | 3092 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor Total | 43092 | --- | 2 | 4Q_FP_PF | R
56 | 220 | Frequency | 3110 | Hz | 2 | FLOAT32 | R | Frequency | 43110 | Hz | 2 | FLOAT32 | R
57 |  | Year | 1837 | year | 1 | INT16U | R | Year | 41837 | year | 1 | INT16U | R | 14
58 |  | Month | 1838 | month | 1 | INT16U | R | Month | 41838 | month | 1 | INT16U | R
59 |  | Day | 1839 | days | 1 | INT16U | R | Day | 41839 | days | 1 | INT16U | R
60 |  | Hour | 1840 | hours | 1 | INT16U | R | Hour | 41840 | hours | 1 | INT16U | R
61 |  | Minute | 1841 | minutes | 1 | INT16U | R | Minute | 41841 | minutes | 1 | INT16U | R
62 |  | Second | 1842 | seconds | 1 | INT16U | R | Second | 41842 | seconds | 1 | INT16U | R
63 |  | Millisecond | 1843 | msec | 1 | INT16U | R | Millisecond | 41843 | msec | 1 | INT16U | R
64 |  | Active Load Timer | 2002 |  |  |  | R | Active Load Timer | 42002 |  |  |  |  | 6
65 |  | Meter Operation Timer | 2004 |  |  |  | R | Meter Operation Timer | 42004
66 |  | Cycle Count | 2006 |  |  |  | R | Cycle Count | 42006
67 |  | Active Energy Delivered (Into Load) | 2700 | kWh | 2 | FLOAT32 | R | Active Energy Delivered (Into Load) | 42700 | kWh | 2 | FLOAT32 | R | 24
68 |  | Active Energy Received (Out of Load) | 2702 | kWh | 2 | FLOAT32 | R | Active Energy Received (Out of Load) | 42702 | kWh | 2 | FLOAT32 | R
69 |  | Active Energy Delivered + Received | 2704 | kWh | 2 | FLOAT32 | R | Active Energy Delivered + Received | 42704 | kWh | 2 | FLOAT32 | R
70 |  | Active Energy Delivered- Received | 2706 | kWh | 2 | FLOAT32 | R | Active Energy Delivered- Received | 42706 | kWh | 2 | FLOAT32 | R
71 |  | Reactive Energy Delivered | 2708 | kVARh | 2 | FLOAT32 | R | Reactive Energy Delivered | 42708 | kVARh | 2 | FLOAT32 | R
72 |  | Reactive Energy Received | 2710 | kVARh | 2 | FLOAT32 | R | Reactive Energy Received | 42710 | kVARh | 2 | FLOAT32 | R
73 |  | Reactive Energy Delivered + Received | 2712 | kVARh | 2 | FLOAT32 | R | Reactive Energy Delivered + Received | 42712 | kVARh | 2 | FLOAT32 | R
74 |  | Reactive Energy Delivered - Received | 2714 | kVARh | 2 | FLOAT32 | R | Reactive Energy Delivered - Received | 42714 | kVARh | 2 | FLOAT32 | R
75 |  | Apparent Energy Delivered | 2716 | kVAh | 2 | FLOAT32 | R | Apparent Energy Delivered | 42716 | kVAh | 2 | FLOAT32 | R
76 |  | Apparent Energy Received | 2718 | kVAh | 2 | FLOAT32 | R | Apparent Energy Received | 42718 | kVAh | 2 | FLOAT32 | R
77 |  | Apparent Energy Delivered + Received | 2720 | kVAh | 2 | FLOAT32 | R | Apparent Energy Delivered + Received | 42720 | kVAh | 2 | FLOAT32 | R
78 |  | Apparent Energy Delivered - Received | 2722 | kVAh | 2 | FLOAT32 | R | Apparent Energy Delivered - Received | 42722 | kVAh | 2 | FLOAT32 | R
79 |  | Accumulated Energy Reset Date/Time | 3200 | --- | 4 | DATETIME | R | Accumulated Energy Reset Date/Time | 43200 | --- | 4 | DATETIME | R | 26
80 |  | Active Energy Delivered (Into Load) | 3204 | Wh | 4 | INT64 | R | Active Energy Delivered (Into Load) | 43204 | Wh | 4 | INT64 | R
81 |  | Active Energy Received (Out of Load) | 3208 | Wh | 4 | INT64 | R | Active Energy Received (Out of Load) | 43208 | Wh | 4 | INT64 | R
82 |  | Active Energy Delivered + Received | 3212 | Wh | 4 | INT64 | R | Active Energy Delivered + Received | 43212 | Wh | 4 | INT64 | R
83 |  | Active Energy Delivered- Received | 3216 | Wh | 4 | INT64 | R | Active Energy Delivered- Received | 43216 | Wh | 4 | INT64 | R
84 |  | Reactive Energy Delivered | 3220 | VARh | 4 | INT64 | R | Reactive Energy Delivered | 43220 | VARh | 4 | INT64 | R
85 |  | Reactive Energy Received | 3224 | VARh | 4 | INT64 | R | Reactive Energy Received | 43224 | VARh | 4 | INT64 | R
86 |  | Reactive Energy Delivered + Received | 3228 | VARh | 4 | INT64 | R | Reactive Energy Delivered + Received | 43228 | VARh | 4 | INT64 | R
87 |  | Reactive Energy Delivered - Received | 3232 | VARh | 4 | INT64 | R | Reactive Energy Delivered - Received | 43232 | VARh | 4 | INT64 | R
88 |  | Apparent Energy Delivered | 3236 | VAh | 4 | INT64 | R | Apparent Energy Delivered | 43236 | VAh | 4 | INT64 | R
89 |  | Apparent Energy Received | 3240 | VAh | 4 | INT64 | R | Apparent Energy Received | 43240 | VAh | 4 | INT64 | R
90 |  | Apparent Energy Delivered + Received | 3244 | VAh | 4 | INT64 | R | Apparent Energy Delivered + Received | 43244 | VAh | 4 | INT64 | R
91 |  | Apparent Energy Delivered - Received | 3248 | VAh | 4 | INT64 | R | Apparent Energy Delivered - Received | 43248 | VAh | 4 | INT64 | R
92 |  | Last Demand | 3764 | kW | 2 | FLOAT32 | R | Last Demand | 43764 | kW | 2 | FLOAT32 | R | 8
93 |  | Present Demand | 3766 | kW | 2 | FLOAT32 | R | Present Demand | 43766 | kW | 2 | FLOAT32 | R
94 |  | Predicted Demand | 3768 | kW | 2 | FLOAT32 | R | Predicted Demand | 43768 | kW | 2 | FLOAT32 | R
95 |  | Peak Demand | 3770 | kW | 2 | FLOAT32 | R | Peak Demand | 43770 | kW | 2 | FLOAT32 | R

## Copy of Sheet1
LEN | ENERGY METER DATA | [5 empty] | TIA PORTAL DATA
| Description | Register | Units | Size (INT16) | Data Type | Access | Description | Register | Units | Size (INT16) | Data Type | Access
0 | Current A | 3000 | A | 2 | FLOAT32 | R | Current A |  | A | 2 | FLOAT32 | R
4 | Current B | 3002 | A | 2 | FLOAT32 | R | Current B |  | A | 2 | FLOAT32 | R
8 | Current C | 3004 | A | 2 | FLOAT32 | R | Current C |  | A | 2 | FLOAT32 | R
12 | Current N | 3006 | A | 2 | FLOAT32 | R | Current N |  | A | 2 | FLOAT32 | R
16 | Current G | 3008 | A | 2 | FLOAT32 | R | Current G |  | A | 2 | FLOAT32 | R
20 | Current Avg | 3010 | A | 2 | FLOAT32 | R | Current Avg |  | A | 2 | FLOAT32 | R
24 | Current Unbalance A | 3012 | % | 2 | FLOAT32 | R | Current Unbalance A |  | % | 2 | FLOAT32 | R
28 | Current Unbalance B | 3014 | % | 2 | FLOAT32 | R | Current Unbalance B |  | % | 2 | FLOAT32 | R
32 | Current Unbalance C | 3016 | % | 2 | FLOAT32 | R | Current Unbalance C |  | % | 2 | FLOAT32 | R
36 | Current Unbalance Worst | 3018 | % | 2 | FLOAT32 | R | Current Unbalance Worst |  | % | 2 | FLOAT32 | R
40 | Voltage A-B | 3020 | V | 2 | FLOAT32 | R | Voltage A-B |  | V | 2 | FLOAT32 | R
44 | Voltage B-C | 3022 | V | 2 | FLOAT32 | R | Voltage B-C |  | V | 2 | FLOAT32 | R
48 | Voltage C-A | 3024 | V | 2 | FLOAT32 | R | Voltage C-A |  | V | 2 | FLOAT32 | R
52 | Voltage L-L Avg | 3026 | V | 2 | FLOAT32 | R | Voltage L-L Avg |  | V | 2 | FLOAT32 | R
56 | Voltage A-N | 3028 | V | 2 | FLOAT32 | R | Voltage A-N |  | V | 2 | FLOAT32 | R
60 | Voltage B-N | 3030 | V | 2 | FLOAT32 | R | Voltage B-N |  | V | 2 | FLOAT32 | R
64 | Voltage C-N | 3032 | V | 2 | FLOAT32 | R | Voltage C-N |  | V | 2 | FLOAT32 | R
68 | Voltage L-N Avg | 3036 | V | 2 | FLOAT32 | R | Voltage L-N Avg |  | V | 2 | FLOAT32 | R
72 | Voltage Unbalance A-B | 3038 | % | 2 | FLOAT32 | R | Voltage Unbalance A-B |  | % | 2 | FLOAT32 | R
76 | Voltage Unbalance B-C | 3040 | % | 2 | FLOAT32 | R | Voltage Unbalance B-C |  | % | 2 | FLOAT32 | R
80 | Voltage Unbalance C-A | 3042 | % | 2 | FLOAT32 | R | Voltage Unbalance C-A |  | % | 2 | FLOAT32 | R
84 | Voltage Unbalance L-L Worst | 3044 | % | 2 | FLOAT32 | R | Voltage Unbalance L-L Worst |  | % | 2 | FLOAT32 | R
88 | Voltage Unbalance A-N | 3046 | % | 2 | FLOAT32 | R | Voltage Unbalance A-N |  | % | 2 | FLOAT32 | R
92 | Voltage Unbalance B-N | 3048 | % | 2 | FLOAT32 | R | Voltage Unbalance B-N |  | % | 2 | FLOAT32 | R
96 | Voltage Unbalance C-N | 3050 | % | 2 | FLOAT32 | R | Voltage Unbalance C-N |  | % | 2 | FLOAT32 | R
100 | Voltage Unbalance L-N Worst | 3052 | % | 2 | FLOAT32 | R | Voltage Unbalance L-N Worst |  | % | 2 | FLOAT32 | R
104 | Active Power A | 3054 | kW | 2 | FLOAT32 | R | Active Power A |  | kW | 2 | FLOAT32 | R
108 | Active Power B | 3056 | kW | 2 | FLOAT32 | R | Active Power B |  | kW | 2 | FLOAT32 | R
112 | Active Power C | 3058 | kW | 2 | FLOAT32 | R | Active Power C |  | kW | 2 | FLOAT32 | R
116 | Active Power Total | 3060 | kW | 2 | FLOAT32 | R | Active Power Total |  | kW | 2 | FLOAT32 | R
120 | Reactive Power A | 3062 | kVAR | 2 | FLOAT32 | R | Reactive Power A |  | kVAR | 2 | FLOAT32 | R
124 | Reactive Power B | 3064 | kVAR | 2 | FLOAT32 | R | Reactive Power B |  | kVAR | 2 | FLOAT32 | R
128 | Reactive Power C | 3066 | kVAR | 2 | FLOAT32 | R | Reactive Power C |  | kVAR | 2 | FLOAT32 | R
132 | Reactive Power Total | 3068 | kVAR | 2 | FLOAT32 | R | Reactive Power Total |  | kVAR | 2 | FLOAT32 | R
136 | Apparent Power A | 3070 | kVA | 2 | FLOAT32 | R | Apparent Power A |  | kVA | 2 | FLOAT32 | R
140 | Apparent Power B | 3072 | kVA | 2 | FLOAT32 | R | Apparent Power B |  | kVA | 2 | FLOAT32 | R
144 | Apparent Power C | 3074 | kVA | 2 | FLOAT32 | R | Apparent Power C |  | kVA | 2 | FLOAT32 | R
148 | Apparent Power Total | 3076 | kVA | 2 | FLOAT32 | R | Apparent Power Total |  | kVA | 2 | FLOAT32 | R
152 | Power Factor A | 3078 | --- | 2 | 4Q_FP_PF | R | Power Factor A |  | --- | 2 | 4Q_FP_PF | R
156 | Power Factor B | 3080 | --- | 2 | 4Q_FP_PF | R | Power Factor B |  | --- | 2 | 4Q_FP_PF | R
160 | Power Factor C | 3082 | --- | 2 | 4Q_FP_PF | R | Power Factor C |  | --- | 2 | 4Q_FP_PF | R
164 | Power Factor Total | 3084 | --- | 2 | 4Q_FP_PF | R | Power Factor Total |  | --- | 2 | 4Q_FP_PF | R
168 | Displacement Power Factor A | 3086 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor A |  | --- | 2 | 4Q_FP_PF | R
172 | Displacement Power Factor B | 3088 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor B |  | --- | 2 | 4Q_FP_PF | R
176 | Displacement Power Factor C | 3090 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor C |  | --- | 2 | 4Q_FP_PF | R
180 | Displacement Power Factor Total | 3092 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor Total |  | --- | 2 | 4Q_FP_PF | R
184 | Frequency | 3110 | Hz | 2 | FLOAT32 | R | Frequency |  | Hz | 2 | FLOAT32 | R

## Energy Meter Data
No. | LEN | ENERGY METER DATA | [5 empty] | TIA PORTAL DATA | [5 empty] | Len
|  | Description | Register | Units | Size (INT16) | Data Type | Access | Description | Register | Units | Size (INT16) | Data Type | Access | 112
1 | 0 | Current A | 3000 | A | 2 | FLOAT32 | R | Current A | 43000 | A | 2 | FLOAT32 | R
2 | 4 | Current B | 3002 | A | 2 | FLOAT32 | R | Current B | 43002 | A | 2 | FLOAT32 | R
3 | 8 | Current C | 3004 | A | 2 | FLOAT32 | R | Current C | 43004 | A | 2 | FLOAT32 | R
4 | 12 | Current N | 3006 | A | 2 | FLOAT32 | R | Current N | 43006 | A | 2 | FLOAT32 | R
5 | 16 | Current G | 3008 | A | 2 | FLOAT32 | R | Current G | 43008 | A | 2 | FLOAT32 | R
6 | 20 | Current Avg | 3010 | A | 2 | FLOAT32 | R | Current Avg | 43010 | A | 2 | FLOAT32 | R
7 | 24 | Current Unbalance A | 3012 | % | 2 | FLOAT32 | R | Current Unbalance A | 43012 | % | 2 | FLOAT32 | R
8 | 28 | Current Unbalance B | 3014 | % | 2 | FLOAT32 | R | Current Unbalance B | 43014 | % | 2 | FLOAT32 | R
9 | 32 | Current Unbalance C | 3016 | % | 2 | FLOAT32 | R | Current Unbalance C | 43016 | % | 2 | FLOAT32 | R
10 | 36 | Current Unbalance Worst | 3018 | % | 2 | FLOAT32 | R | Current Unbalance Worst | 43018 | % | 2 | FLOAT32 | R
11 | 40 | Voltage A-B | 3020 | V | 2 | FLOAT32 | R | Voltage A-B | 43020 | V | 2 | FLOAT32 | R
12 | 44 | Voltage B-C | 3022 | V | 2 | FLOAT32 | R | Voltage B-C | 43022 | V | 2 | FLOAT32 | R
13 | 48 | Voltage C-A | 3024 | V | 2 | FLOAT32 | R | Voltage C-A | 43024 | V | 2 | FLOAT32 | R
14 | 52 | Voltage L-L Avg | 3026 | V | 2 | FLOAT32 | R | Voltage L-L Avg | 43026 | V | 2 | FLOAT32 | R
15 | 56 | Voltage A-N | 3028 | V | 2 | FLOAT32 | R | Voltage A-N | 43028 | V | 2 | FLOAT32 | R
16 | 60 | Voltage B-N | 3030 | V | 2 | FLOAT32 | R | Voltage B-N | 43030 | V | 2 | FLOAT32 | R
17 | 64 | Voltage C-N | 3032 | V | 2 | FLOAT32 | R | Voltage C-N | 43032 | V | 2 | FLOAT32 | R
18 | 68 | Not use | 3034 | --- | - | - | - | - | 43034 | --- | - | - | -
19 | 72 | Voltage L-N Avg | 3036 | V | 2 | FLOAT32 | R | Voltage L-N Avg | 43036 | V | 2 | FLOAT32 | R
20 | 76 | Voltage Unbalance A-B | 3038 | % | 2 | FLOAT32 | R | Voltage Unbalance A-B | 43038 | % | 2 | FLOAT32 | R
21 | 80 | Voltage Unbalance B-C | 3040 | % | 2 | FLOAT32 | R | Voltage Unbalance B-C | 43040 | % | 2 | FLOAT32 | R
22 | 84 | Voltage Unbalance C-A | 3042 | % | 2 | FLOAT32 | R | Voltage Unbalance C-A | 43042 | % | 2 | FLOAT32 | R
23 | 88 | Voltage Unbalance L-L Worst | 3044 | % | 2 | FLOAT32 | R | Voltage Unbalance L-L Worst | 43044 | % | 2 | FLOAT32 | R
24 | 92 | Voltage Unbalance A-N | 3046 | % | 2 | FLOAT32 | R | Voltage Unbalance A-N | 43046 | % | 2 | FLOAT32 | R
25 | 96 | Voltage Unbalance B-N | 3048 | % | 2 | FLOAT32 | R | Voltage Unbalance B-N | 43048 | % | 2 | FLOAT32 | R
26 | 100 | Voltage Unbalance C-N | 3050 | % | 2 | FLOAT32 | R | Voltage Unbalance C-N | 43050 | % | 2 | FLOAT32 | R
27 | 104 | Voltage Unbalance L-N Worst | 3052 | % | 2 | FLOAT32 | R | Voltage Unbalance L-N Worst | 43052 | % | 2 | FLOAT32 | R
28 | 108 | Active Power A | 3054 | kW | 2 | FLOAT32 | R | Active Power A | 43054 | kW | 2 | FLOAT32 | R
29 | 112 | Active Power B | 3056 | kW | 2 | FLOAT32 | R | Active Power B | 43056 | kW | 2 | FLOAT32 | R
30 | 116 | Active Power C | 3058 | kW | 2 | FLOAT32 | R | Active Power C | 43058 | kW | 2 | FLOAT32 | R
31 | 120 | Active Power Total | 3060 | kW | 2 | FLOAT32 | R | Active Power Total | 43060 | kW | 2 | FLOAT32 | R
32 | 124 | Reactive Power A | 3062 | kVAR | 2 | FLOAT32 | R | Reactive Power A | 43062 | kVAR | 2 | FLOAT32 | R
33 | 128 | Reactive Power B | 3064 | kVAR | 2 | FLOAT32 | R | Reactive Power B | 43064 | kVAR | 2 | FLOAT32 | R
34 | 132 | Reactive Power C | 3066 | kVAR | 2 | FLOAT32 | R | Reactive Power C | 43066 | kVAR | 2 | FLOAT32 | R
35 | 136 | Reactive Power Total | 3068 | kVAR | 2 | FLOAT32 | R | Reactive Power Total | 43068 | kVAR | 2 | FLOAT32 | R
36 | 140 | Apparent Power A | 3070 | kVA | 2 | FLOAT32 | R | Apparent Power A | 43070 | kVA | 2 | FLOAT32 | R
37 | 144 | Apparent Power B | 3072 | kVA | 2 | FLOAT32 | R | Apparent Power B | 43072 | kVA | 2 | FLOAT32 | R
38 | 148 | Apparent Power C | 3074 | kVA | 2 | FLOAT32 | R | Apparent Power C | 43074 | kVA | 2 | FLOAT32 | R
39 | 152 | Apparent Power Total | 3076 | kVA | 2 | FLOAT32 | R | Apparent Power Total | 43076 | kVA | 2 | FLOAT32 | R
40 | 156 | Not use | Not use
41 | 160 | Not use | Not use | [5 empty] | #VALUE!
42 | 164 | Not use | Not use | [5 empty] | #VALUE!
43 | 168 | Not use | Not use | [5 empty] | #VALUE!
44 | 172 | Not use | Not use | [5 empty] | #VALUE!
45 | 176 | Not use | Not use | [5 empty] | #VALUE!
46 | 180 | Not use | Not use | [5 empty] | #VALUE!
47 | 184 | Not use | Not use | [5 empty] | #VALUE!
48 | 188 | Power Factor A | 3078 | --- | 2 | 4Q_FP_PF | R | Power Factor A | 43078 | --- | 2 | 4Q_FP_PF | R
49 | 192 | Power Factor B | 3080 | --- | 2 | 4Q_FP_PF | R | Power Factor B | 43080 | --- | 2 | 4Q_FP_PF | R
50 | 196 | Power Factor C | 3082 | --- | 2 | 4Q_FP_PF | R | Power Factor C | 43082 | --- | 2 | 4Q_FP_PF | R
51 | 200 | Power Factor Total | 3084 | --- | 2 | 4Q_FP_PF | R | Power Factor Total | 43084 | --- | 2 | 4Q_FP_PF | R
52 | 204 | Displacement Power Factor A | 3086 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor A | 43086 | --- | 2 | 4Q_FP_PF | R
53 | 208 | Displacement Power Factor B | 3088 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor B | 43088 | --- | 2 | 4Q_FP_PF | R
54 | 212 | Displacement Power Factor C | 3090 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor C | 43090 | --- | 2 | 4Q_FP_PF | R
55 | 216 | Displacement Power Factor Total | 3092 | --- | 2 | 4Q_FP_PF | R | Displacement Power Factor Total | 43092 | --- | 2 | 4Q_FP_PF | R
56 | 220 | Frequency | 3110 | Hz | 2 | FLOAT32 | R | Frequency | 43110 | Hz | 2 | FLOAT32 | R